## 200SF Calculator Tool
Assumptions
*Room as a single, well-mixed compartment (box model)
*Steady state in inputs, equilibrium for outputs calculation
*NTP conditions
Assumed Supply Air CO2 conc | 400 | ppm
Avg CO2 emission rate / hour | 30 | g/h per person | Link to Calculator
Avg CO2 emission rate / min | 0.5 | g/min
Air -moles per m3 | 41.6 | At NTP
m3 per ft3 | 0.028317 | unit conv
Air - moles per ft^3 | 1.178
Design Occupancy (Medium Conference Room @ 40SF/Seat)
Seats | 5
Area (SF) | 200
|  | Conventional | Enhanced | Stringent*
Personal Rate | CFM/Seat | 5 | 6.5 | 15 | * CA Title 24 is the greater of personal and area rates (vs. ASHRAE which is combined)
Area Rate | CFM/SF | 0.06 | 0.078 | 0.15
Ventilation Rate (Personal + Area) | CFM/Seat | 7.4 | 9.62 | 15
Area Rate | CFM min for 200SF space | 12
Vent Rate per person | CFM /seat added | 5
Modeled indoor CO2 concentration | g/cubic-feet | 0.067568 | 0.051975 | 0.033333
Indoor CO2 -moles-CO2/ft^3-air |  | 0.0015356 | 0.0011813 | 0.00075758
Indoor CO2 increment - molesCO2/molesAir *10^6 | ppm | 1303.6091 | 1002.7762 | 643.1138
CO2 Limit @ Design Occupancy | ppm | 1703.6091 | 1402.7762 | 1043.1138
Actual Occupancy - What happens if you pack the room?
|  | Conventional | Enhanced | Stringent
Actual Occupancy |  | 5 | 8 | 13
Modeled indoor CO2 concentration | g/cubic-feet | 0.067568 | 0.08316 | 0.086667
Indoor CO2 -moles-CO2/ft^3-air |  | 0.0015356 | 0.00189 | 0.0019697
Indoor CO2 increment - molesCO2/molesAir *10^6 | ppm | 1303.6091 | 1604.442 | 1672.096
CO2 Limit @ Design Occupancy | ppm | 1703.6091 | 2004.442 | 2072.096
PART 1 - Conf Room CFM at Varying Occupancy
| SF Room | 200
| Design Occupancy | Conventional | Enhanced | Stringent
| 0 | 12 | 15.6 | 30
| 1 | 17 | 22.1 | 30
| 2 | 22 | 28.6 | 30
| 3 | 27 | 35.1 | 45
| 4 | 32 | 41.6 | 60
| 5 | 37 | 48.1 | 75
| 6 | 42 | 54.6 | 90
| 7 | 47 | 61.1 | 105
| 8 | 52 | 67.6 | 120
| 9 | 57 | 74.1 | 135
| 10 | 62 | 80.6 | 150
PART 2 - Conf Room CO2 at Varying Design Occupancy
| Design Occupancy | Conventional | Enhanced | Stringent*
| 0 | 400 | 400 | 400
| 1 | 967.4534 | 836.5026 | 721.5569
| 2 | 1276.9734 | 1074.5949 | 1043.1138
| 3 | 1471.8564 | 1224.5049 | 1043.1138
| 4 | 1605.8384 | 1327.568 | 1043.1138
| 5 | 1703.6091 | 1402.7762 | 1043.1138
| 6 | 1778.1011 | 1460.0777 | 1043.1138
| 7 | 1836.7437 | 1505.1874 | 1043.1138
| 8 | 1884.1088 | 1541.6222 | 1043.1138
| 9 | 1923.1643 | 1571.6649 | 1043.1138
| 10 | 1955.9206 | 1596.862 | 1043.1138
*Stringent case stays constant once the ventilation rate is being scaled by occupancy, as the emissions are scaling by occupancy (so the two cancel out)
PART 3 - Conf Room CO2 at Varying Actual Occupancy
| Actual Occupancy | Conventional | Enhanced | Stringent*
| 0 | 400 | 400 | 400
| 1 | 660.7218 | 600.5552 | 528.6228
| 2 | 921.4436 | 801.1105 | 657.2455
| 3 | 1182.1655 | 1001.6657 | 785.8683
| 4 | 1442.8873 | 1202.221 | 914.4911
| 5 | 1703.6091 | 1402.7762 | 1043.1138
| 6 | 1964.3309 | 1603.3315 | 1171.7366
| 7 | 2225.0528 | 1803.8867 | 1300.3594
| 8 | 2485.7746 | 2004.442 | 1428.9821
| 9 | 2746.4964 | 2204.9972 | 1557.6049
| 10 | 3007.2182 | 2405.5525 | 1686.2277
Note on B47: Nice to vary -Michael Bloom - M1G
Note on C27: BrianMGilligan:
Note on C76: Need to vary -Michael Bloom - M1G

## 1000SF Office Tool
Assumptions
*Room as a single, well-mixed compartment (box model)
*Steady state in inputs, equilibrium for outputs calculation
*NTP conditions
Assumed Supply Air CO2 conc | 400 | ppm
Avg CO2 emission rate / hour | 30 | g/h per person | Link to Calculator
Avg CO2 emission rate / min | 0.5 | g/min
Air -moles per m3 | 41.6 | At NTP
m3 per ft3 | 0.028317 | unit conv
Air - moles per ft^3 | 1.178
Design Occupancy (Medium Conference Room @ 40SF/Seat)
Seats | 5
Area (SF) | 1000
|  | Conventional | Enhanced | Stringent*
Personal Rate | CFM/Seat | 5 | 6.5 | 15 | * CA Title 24 is the greater of personal and area rates (vs. ASHRAE which is combined)
Area Rate | CFM/SF | 0.06 | 0.078 | 0.15
Ventilation Rate (Personal + Area) | CFM/Seat | 17 | 22.1 | 30
Area Rate | CFM min for 200SF space | 60
Vent Rate per person | CFM /seat added | 5
Modeled indoor CO2 concentration | g/cubic-feet | 0.029412 | 0.022624 | 0.016667
Indoor CO2 -moles-CO2/ft^3-air |  | 0.00066845 | 0.00051419 | 0.00037879
Indoor CO2 increment - molesCO2/molesAir *10^6 | ppm | 567.4534 | 436.5026 | 321.5569
CO2 Limit @ Design Occupancy | ppm | 967.4534 | 836.5026 | 721.5569
Actual Occupancy - What happens if you pack the room?
|  | Conventional | Enhanced | Stringent
Actual Occupancy |  | 5 | 6 | 13
Modeled indoor CO2 concentration | g/cubic-feet | 0.029412 | 0.027149 | 0.043333
Indoor CO2 -moles-CO2/ft^3-air |  | 0.00066845 | 0.00061703 | 0.00098485
Indoor CO2 increment - molesCO2/molesAir *10^6 | ppm | 567.4534 | 523.8031 | 836.048
CO2 Limit @ Design Occupancy | ppm | 967.4534 | 923.8031 | 1236.048
PART 1 - Conf Room CFM at Varying Occupancy
| SF Room | 1000
| Design Occupancy | Conventional | Enhanced | Stringent
| 0 | 60 | 78 | 150
| 2 | 70 | 91 | 150
| 5 | 85 | 110.5 | 150
| 6 | 90 | 117 | 150
| 8 | 100 | 130 | 150
| 10 | 110 | 143 | 150
| 12 | 120 | 156 | 180
| 14 | 130 | 169 | 210
| 16 | 140 | 182 | 240
| 18 | 150 | 195 | 270
| 20 | 160 | 208 | 300
PART 2 - Conf Room CO2 at Varying Design Occupancy
| Design Occupancy | Conventional | Enhanced | Stringent*
| 0 | 400 | 400 | 400
| 2 | 675.6202 | 612.0155 | 528.6228
| 5 | 967.4534 | 836.5026 | 721.5569
| 6 | 1043.1138 | 894.7029 | 785.8683
| 8 | 1171.7366 | 993.6435 | 914.4911
| 10 | 1276.9734 | 1074.5949 | 1043.1138
| 12 | 1364.6707 | 1142.0544 | 1043.1138
| 14 | 1438.8762 | 1199.1355 | 1043.1138
| 16 | 1502.4809 | 1248.0622 | 1043.1138
| 18 | 1557.6049 | 1290.4653 | 1043.1138
| 20 | 1605.8384 | 1327.568 | 1043.1138
*Stringent case stays constant once the ventilation rate is being scaled by occupancy, as the emissions are scaling by occupancy (so the two cancel out)
PART 3 - Conf Room CO2 at Varying Actual Occupancy
| Actual Occupancy | Conventional | Enhanced | Stringent*
| 0 | 400 | 400 | 400
| 2 | 626.9814 | 574.601 | 528.6228
| 5 | 967.4534 | 836.5026 | 721.5569
| 6 | 1080.9441 | 923.8031 | 785.8683
| 8 | 1307.9254 | 1098.4042 | 914.4911
| 10 | 1534.9068 | 1273.0052 | 1043.1138
| 12 | 1761.8881 | 1447.6062 | 1171.7366
| 14 | 1988.8695 | 1622.2073 | 1300.3594
| 16 | 2215.8508 | 1796.8083 | 1428.9821
| 18 | 2442.8322 | 1971.4094 | 1557.6049
| 20 | 2669.8135 | 2146.0104 | 1686.2277
Note on C27: BrianMGilligan: